# CHN1A PROJECT - PERMIT TRACKER ANALYSIS & RECOMMENDATIONS

**Project:** GFL Cut-In (CHN1A)

**Analysis Date:** June 30, 2026

**Document Purpose:** Comparative analysis of actual permits vs. comprehensive guide recommendations

---

# EXECUTIVE SUMMARY

Your CHN1A project is tracking **14 permits** across a condensed **9-month timeline** (April 2026 - January 2027). This is significantly shorter than the 24-32 month typical for data center projects documented in the comprehensive guides, indicating either:

1. This is a modular/phased project (not full build)

2. Major permitting is already completed (BOI, EIA, Building Permit)

3. You're focusing on operational/commissioning permits only

## Key Observations

✅ Most critical infrastructure permits are tracking well

⚠️ Some permits show schedule compression (tight timelines)

❌ Missing permits from comprehensive guide not addressed

📊 Current planned completion: January 27, 2027 (for major operating permits)

---

# SECTION 1: PERMIT-BY-PERMIT MAPPING TO COMPREHENSIVE GUIDE

## Permit 1: Building Construction Permit - Make-up Water Tank (IEAT 02/2)

**Your Status:** ✅ DONE

Submitted by: GC (General Contractor)

Authority: AHJ (Authority Having Jurisdiction), IEAT

Planned duration: 65-95 days

Outcome: Complete

**Comprehensive Guide Reference:** Part 3 (Building Permits)

Guide predicted: 6-10 weeks ✅ Matches (65-95 days = 9-13 weeks)

Note: Water tank classification as "building" when >10m high is correct per Thai building code

**Status:** On Track

---

## Permit 2: Building Construction Certificate/Occupancy Permit (IEAT 02/6)

**Your Status:** ⏳ IN PROGRESS

Submitted by: GC

Authority: AHJ, IEAT

Planned duration: 60 days

Timeline: POA Aug 15 → Submit Oct 14 → Receive Jan 27, 2027

**Comprehensive Guide Reference:** Part 3, Section 3.7 (Building Permit)

Guide predicted: 6-10 weeks ✅ Matches

**CRITICAL:** This is the master occupancy permit - gates operations start

Cannot operate facility without this

**Analysis:**

⚠️ Timeline shows very long tail (Oct 14 submission to Jan 27 receipt = 3.5 months)

This exceeds typical 60-day processing

Possible reasons:

- Sequential processing (not parallel with other permits)

- Pending inspection/approval of other systems first

- IEAT coordination delays common in Thailand

**Recommendation:**

Verify with AHJ/IEAT if 60-day timeline is still realistic

If delays likely, escalate now rather than discovering in October

Ensure all pre-submission inspections completed (fire, electrical, structural)

**Status:** ⚠️ MONITOR - Timeline appears loose

---

## Permit 3: Power Energize/Supply (PEA Connection)

**Your Status:** ✅ DONE

Submitted by: GC

Authority: PEA

Planned duration: 14 days

Outcome: Completed May 1, 2026

**Comprehensive Guide Reference:** Part 4, Section 4.3 (Power Utility Connection)

Guide predicted: 8-16 weeks for complex infrastructure

Your actual: 14 days ✅ MUCH FASTER

**Analysis:**

✅ Excellent execution - this is power connection (not substation)

14-day timeline is standard for normal capacity projects

Suggests pre-coordination with PEA was excellent

May indicate single-feed (not dual-feed redundancy)

**Recommendation:**

If not already done: Verify dual-feed isn't needed for data center reliability

Dual-feed requires second separate connection (would add 4-8 weeks)

Document why single feed adequate for your use case

**Status:** ✅ COMPLETE - Well Managed

---

## Permit 4: Operating Permit of Electricity Supply (Generator - PorKor1 > 200 kVA)

**Your Status:** ⏳ IN PROGRESS

Submitted by: GG (likely Project Owner)

Authority: DEDE (Department of Energy Development and Efficiency)

Planned duration: 60 days (listed), but 180 days in details

Timeline: POA May 18 → Submit Jun 24 → Receive Aug 14 → NBD Aug 15

**Comprehensive Guide Reference:** Part 4, Section 4.4 (Generator License)

Guide predicted: 4-8 weeks ✅ Matches (60 days / ~9 weeks)

**Note:** 180-day duration in spreadsheet details may be annual compliance, not initial approval

**Analysis:**

Timeline shows POA → Submission = 37 days (normal)

Submission → Approval = 51 days (within 60-day estimate) ✅

Construction/As-built drawings must be complete (per your notes) ✅

**Key Requirements Met (per your tracker):**

EYD (electrical yard) drawings must be completed first

Construction and As-built drawings required

**Recommendation:**

Confirm EYD area drawings are on track (gates this permit)

Generator emission testing may be required (stack test) - budget 1-2 weeks

Verify fuel storage permits are coordinated (see Permit 11)

**Status:** ✅ ON TRACK - Well Paced

---

## Permit 5: Water Supply (WHA - Water Authority)

**Your Status:** ⏳ IN PROGRESS (WIP)

Submitted by: GC

Authority: WHA (Water Authority)

Planned duration: 30 days

Timeline: POA Jun 3 → Submit Jul 20 → Receive Aug 3 → NBD Aug 10, 2026

Note: "Done for temporary / WHA is processing supplier sourcing"

**Comprehensive Guide Reference:** Part 5, Section 5.2 (Water Supply Connection)

Guide predicted: 4-8 weeks ✅ Matches (30 days = ~4 weeks)

**Analysis:**

✅ Temporary connection already approved (smart move)

WHA now processing permanent supplier sourcing

Indicates you're operating on temporary while permanent infrastructure routes

Supply routing can take 1-2 months (hence Aug 10 NBD)

**Key Items to Verify:**

Capacity: What daily water demand (liters/day)? Compare to WHA available supply

Treatment: Do you have water quality pre-treatment? (for cooling systems)

Recycling: Are you recycling cooling tower water to reduce fresh water demand?

**Recommendation:**

If water demand is high (>100 m³/day), coordinate with WHA on phasing

Ensure treatment system is ready by Aug 10 to receive permanent connection

Budget for water pipeline connection fees (typically THB 50K-200K)

**Status:** ✅ ON TRACK - Temporary already live

---

## Permit 6: Ingress & Egress Connection to the Public (WHA)

**Your Status:** ⏳ IN PROGRESS (WIP)

Submitted by: GC

Authority: WHA

Planned duration: 30 days

Timeline: POA Jun 15 → Submit Sep 24 → Receive Oct 8 → NBD Oct 15, 2026

Note: "Done for temporary / GC is working on WHA's feedback"

**Comprehensive Guide Reference:** Part 5, Section 5.2 (Water Infrastructure)

Guide doesn't specifically address ingress/egress (UNIQUE TO YOUR PROJECT)

This is access point for water entry to facility from public water line

**Analysis:**

POA to Submit delay: Jun 15 → Sep 24 = **101 days** (unusual gap)

Possible reasons:

- WHA feedback requires design modifications

- Coordination with site access construction

- Environmental/flooding impact assessment

Approval timeline: Sep 24 → Oct 8 = **14 days** (faster than expected)

**Recommendation:**

Verify: What is the hold-up between POA (Jun 15) and submission (Sep 24)?

If GC is "working on WHA's feedback", confirm scope of revisions

May need to accelerate - 3+ month delay could impact operations schedule

**Status:** ⚠️ MONITOR - Long POA-to-submission gap

---

## Permit 7: Site/Storm Drainage Connection to the Public (WHA)

**Your Status:** ⏳ IN PROGRESS (WIP)

Submitted by: GC

Authority: WHA

Planned duration: 30 days

Timeline: POA Jun 15 → Submit Aug 9 → Receive Sep 8 → NBD Sep 15, 2026

**Comprehensive Guide Reference:** Part 3, Section 3.9 (Construction Timeline) + Part 5 (Environmental)

Guide doesn't specifically cover drainage (part of stormwater management)

Should be addressed in EIA mitigation measures

**Analysis:**

POA to Submit: Jun 15 → Aug 9 = 55 days (2 months - reasonable)

Submit to Approve: Aug 9 → Sep 8 = 30 days (exactly as planned) ✅

Similar to Permit 6, WHA feedback required ("GC is working on WHA's feedback")

**Key Questions:**

Is drainage design compliant with EIA stormwater management plan?

Do you have stormwater detention/treatment required by EIA?

Flooding risk assessment completed?

**Recommendation:**

Ensure stormwater design is finalized before Aug 9 submission deadline

Coordinate with environmental team (EIA compliance)

Budget for stormwater treatment system (if required): THB 1-3M

**Status:** ✅ ON TRACK - Timeline reasonable for environmental review

---

## Permit 8: Wastewater Discharge Permit (WHA)

**Your Status:** ⏳ IN PROGRESS (WIP)

Submitted by: GC

Authority: WHA

Planned duration: 30 days

Timeline: POA Jun 15 → Submit Aug 9 → Receive Sep 8 → NBD Sep 15, 2026

**Comprehensive Guide Reference:** Part 5, Section 5.4 (Wastewater Discharge Permit)

Guide predicted: 6-10 weeks ✅ Matches (30 days submission + pre-design work)

**Analysis:**

Same timeline as Permit 7 (likely submitted together - good coordination)

Wastewater quality standards per Part 5:

- BOD: 50 mg/L

- COD: 150 mg/L

- TSS: 50 mg/L

- pH: 6.5-8.5

**Key Requirements (from comprehensive guide):**

1. ✅ Wastewater characterization plan

2. ✅ Treatment system design and capacity

3. ✅ Monitoring plan

4. ? Discharge point (sewer vs. river) - not specified in your tracker

**Recommendation:**

Verify discharge point: To municipal sewer (easier) or to river (harder)?

Confirm wastewater treatment system design is finalized

Budget for treatment: THB 2-5M (typical for facility your size)

Post-opening: Budget for monthly monitoring (THB 3-5K/month)

**Status:** ✅ ON TRACK - Good pace

---

## Permit 9: Business Operation Commencing Permit (IEAT 03/2)

**Your Status:** ⏳ IN PROGRESS

Submitted by: GC

Authority: IEAT

Planned duration: 30 days

Timeline: POA Nov 19 → Submit Dec 23 → Receive Jan 22 → NBD Jan 27, 2027

**Comprehensive Guide Reference:** Part 1 (BOI) + Part 10 (Operational Permits)

Guide indicates: Operational permits follow building completion

IEAT 03/2 is the master "permission to operate" document

**Analysis:**

⚠️ Very late in schedule (Jan 27, 2027)

**CRITICAL:** Cannot legally operate until this is approved

Dependency: Building Certificate (Permit 2) must be done first

Timeline shows: Building cert due Jan 27, operations permit due Jan 27 (synchronized) ✅

**Key Requirements:**

Building occupancy certificate complete

All safety systems operational (fire, electrical, etc.)

All environmental systems operational

Staff trained

Operational procedures documented

**Recommendation:**

**CRITICAL:** Ensure Building Certificate (Permit 2) is on track

If Building Cert delays, operations permit is automatically delayed

Have all supporting documents ready by Nov 19 (POA date)

Small delay in building permit = major operational delay

**Status:** ⚠️ CRITICAL DEPENDENCY - Monitor Building Permit closely

---

## Permit 10: Health Harmful Business Permit (Aor Por 1)

**Your Status:** ⏳ IN PROGRESS

Submitted by: GC

Authority: AHJ (Authority Having Jurisdiction - Local Health Dept)

Planned duration: 30 days

Timeline: POA Aug 14 → Submit Sep 20 → Receive Oct 20 → NBD Oct 27, 2026

**Comprehensive Guide Reference:** Part 3, Section 3.7 (Fire Safety & Prevention Permits)

Guide addresses health/safety compliance generally

Aor Por 1 is Thai Health Ministry form for "harmful businesses"

**Analysis:**

✅ Timeline reasonable (30 days)

Data centers may not technically be "harmful business" - verify classification

**Question:** Why does your project require Aor Por 1?

- Electrical hazards?

- Chemical storage (transformers, batteries)?

- Fuel storage (generator)?

- Other?

**Typical Requirements for Aor Por 1:**

Site plan showing hazard areas

Safety equipment documentation

Emergency response procedures

Health safety management plan

Waste disposal plan

**Recommendation:**

Clarify with AHJ: Does data center actually need Aor Por 1?

If yes, what specific hazard triggers it (likely fuel storage or chemicals)

Ensure all hazardous materials documented and storage compliant

Cross-reference with Permit 11 (Fuel Oil Storage) and Permit 12 (Waste Disposal)

**Status:** ✅ ON TRACK - Timeline reasonable

---

## Permit 11: Fuel Oil Storage Tank Construction (DOEB Stage 2)

**Your Status:** ⏳ IN PROGRESS

Submitted by: GG (Owner/Developer)

Authority: DOEB (Department of Energy Business - now Energy Ministry)

Planned duration: 60 days

Timeline: POA May 18 → Submit Jun 24 → Receive Aug 14 → NBD Aug 15, 2026

Special note: "Construction and As-built drawing must be completed (EYD area)"

Contractor note: "Cummins appointed UBC as representative; 45-day inspection process expected"

**Comprehensive Guide Reference:** Part 4, Section 4.4 (Generator License)

Fuel storage is companion to generator licensing

Generator size >200 kVA is covered by DEDE

Fuel storage >500,000 L covered by DOEB (your case)

**Analysis:**

500,000+ L fuel tank is a major installation

DOEB has two stages:

- **Stage 1:** Design approval (before construction) - appears done

- **Stage 2:** Post-construction inspection (what you're tracking) ✅

Timeline realistic: Construction → 45-day inspection = 75 days ✅

**Key Requirements:**

Construction and As-built drawings for fuel tank

Tank integrity inspection (hydrostatic test typically)

Secondary containment inspection (100% tank capacity)

Fuel quality testing systems

Safety/spill response equipment

**Recommendation:**

Ensure as-built drawings prepared immediately after tank construction completes

Schedule inspection well ahead (DOEB can be slow)

Budget for inspection costs: THB 50-100K

Post-opening: Quarterly fuel quality testing required (THB 5-10K/test)

Maintain secondary containment integrity (annual inspection)

**Status:** ✅ ON TRACK - Contractor (Cummins/UBC) managing well

---

## Permit 12: Waste Disposal

**Your Status:** ⏳ IN PROGRESS

Submitted by: GC

Authority: AHJ (Local Authority) + DIW (Department of Industrial Works)

Planned duration: 30-35 days

Timeline: POA Oct 13 → Submit Dec 16 → Receive Jan 20 → NBD Jan 27, 2027

**Comprehensive Guide Reference:** Part 3 (Environmental Permits) + Part 5 (Environmental Compliance)

Guide Section 5.5: Hazardous Waste Management

**Analysis:**

⏳ Very late in schedule (Dec-Jan)

POA to Submit gap: Oct 13 → Dec 16 = 64 days (2+ months unusual)

Approval timeline: Dec 16 → Jan 20 = 35 days (longer than typical 30) ⚠️

**Key Questions:**

What waste streams are you disposing of?

- Non-hazardous (ordinary)

- Hazardous (transformer oil, batteries, electronics)?

- Both?

Do you have licensed waste contractors identified?

Waste disposal plan approved by EIA?

**Typical Waste Categories for Data Centers:**

General office waste (non-hazardous)

E-waste (computers, servers - potentially hazardous due to metals)

Batteries (hazardous - UPS, emergency lighting)

Transformer oil (if oil-filled transformers - hazardous)

Coolant liquids (potentially hazardous)

Cleaning materials (potentially hazardous)

**Recommendation:**

**URGENT:** Identify specific waste streams now (not in Dec)

Secure licensed waste contractors early (some have capacity limits)

Estimated annual cost: THB 100-300K depending on waste volume

Post-opening: Waste disposal records must be maintained 3 years

Monthly hazardous waste documentation required

**Status:** ⚠️ MONITOR - Late timeline, needs early planning

---

## Permit 13: Radio Communication Equipment License (NBTC)

**Your Status:** ⏳ IN PROGRESS

Submitted by: GC

Authority: NBTC (National Broadcasting and Telecommunications Commission)

Planned duration: 30 days

Timeline: POA Aug 14 → Submit Sep 20 → Receive Oct 20 → NBD Oct 27, 2026

Special note: "Only for walkie-talkie; Other licensing taken care of by 3rd party of GG"

**Comprehensive Guide Reference:** Part 6 (Telecommunications & ICT Permits)

Guide Section 6.3-6.5: Telecom licensing (NBTC)

**Analysis:**

✅ Walkie-talkie licensing is low-complexity (RF equipment license)

Frequency: Typically industrial/construction frequencies (not public)

Cost: Minimal (THB 5-10K)

Processing: 30 days is standard ✅

**Note:** 3rd party managing other telecom (likely ISP or carrier interconnection)

**Key Points:**

Walkie-talkies for site operations/security

Not ISP or carrier service

Lower regulatory burden than commercial telecom

**Questions:**

What "other licensing" is 3rd party handling?

- ISP connectivity?

- International gateway?

- Carrier interconnection?

If major telecom service being provided, that's higher complexity

**Recommendation:**

Confirm scope of "other licensing" with 3rd party (GG's telecom provider)

If ISP service: May require ISP registration (simpler than license)

If international connectivity: May require international gateway license (complex)

Budget: THB 5-10K for walkie-talkie; cost depends on scope of other services

**Status:** ✅ ON TRACK - Straightforward permitting

---

## Permit 14: House Registration (Property Registration)

**Your Status:** ✅ COMPLETE

Submitted by: GC

Authority: AHJ, SAO (Local Authority, Sub-district Office)

Planned duration: 7-15 days

Timeline: POA May 8 → Done by Jun 24, 2026

Status: **Done** - Actual completion Apr 10, 2026

**Comprehensive Guide Reference:** Part 3 (Land/Property Documents)

Not explicitly covered (property registration is prerequisite, not permit)

**Analysis:**

✅ Completed very efficiently (40+ days early)

House registration = property's legal existence documentation

Required before most other permits

**Status:** ✅ COMPLETE - Well executed

---

# SECTION 2: CRITICAL PERMITS MISSING FROM YOUR TRACKER

Based on the comprehensive guide, your CHN1A tracker is **missing** several permits that may already be completed or may be needed:

## MISSING PERMIT 1: Board of Investment (BOI) Promotion Certificate ❓

**Guide Reference:** Part 1 (Complete section on BOI)

**Status in Your Project:** NOT TRACKED

Is this already approved?

If yes: Should be documented (tax exemption proof needed for utilities, work permits)

If no: This should be #1 priority (16-week approval timeline)

**Critical for:**

Tax incentives (8-year corporate income tax holiday)

Work permit facilitation

Utility connection priority with PEA/WHA

Import duty exemptions on equipment

**Recommendation:**

**IMMEDIATE:** Confirm BOI status

If not approved: This is critical path item

If approved: File Certificate copy in project records

---

## MISSING PERMIT 2: Environmental Impact Assessment (EIA) ❓

**Guide Reference:** Part 8 (Complete detailed guide)

**Status in Your Project:** NOT TRACKED

Were environmental permits pre-approved?

No EIA Approval Certificate mentioned

Building permits typically require EIA approval

**Questions:**

Was EIA required for your facility?

If yes, when was it approved?

If no, was EIA screening completed and exemption documented?

**If EIA Was Required - You Need:**

ONEP EIA Approval Certificate

Annual environmental monitoring reports (due next year)

Mitigation measures implementation plan

Compliance verification

**Recommendation:**

**URGENT:** Confirm EIA status

If required but not tracked: Get approval documentation

Budget for annual monitoring compliance (THB 50-100K/year for 5 years minimum)

---

## MISSING PERMIT 3: Foreign Business License (FBL) ❓

**Guide Reference:** Part 2 + PERMIT_02 Detailed Guide

**Status in Your Project:** NOT TRACKED

Is GG a foreign company (>50% foreign ownership)?

Is GG providing colocation services to third parties?

**If Yes to both:**

FBL is REQUIRED (not optional)

8-12 week application timeline

Must be approved before water/utility connections

**Questions to Answer:**

1. Is GG foreign-owned?

2. Is facility for commercial colocation (8.2.1.2) or internal use (8.2.1.1)?

3. If commercial: Was FBL approved?

**Recommendation:**

**IMMEDIATE:** Confirm FBL status

If required but not tracked: This is a compliance gap

If approved: File documentation

---

## MISSING PERMIT 4: Building Permit/Construction License ❓

**Guide Reference:** Part 3, Sections 3.4-3.5

**Status in Your Project:** NOT EXPLICITLY TRACKED

Permit 1 (Water Tank) implies building permits exist

Permit 2 (Occupancy) implies building permits were approved

But main "Building Construction Permit" not in top-level tracker

**Assumptions:**

Main building permit for primary structure (Permit 2: IEAT 02/6) = building permit ✅

Construction license should be approved (not tracked individually)

**Recommendation:**

Verify main building permit is fully approved

Construction license should be documented separately

---

## MISSING PERMIT 5: Electrical Design Approval & Final Inspection

**Guide Reference:** Part 4, Section 4.2 (Electrical)

**Status in Your Project:** NOT TRACKED

Permit 4 (Generator) requires electrical drawings

But no separate electrical design approval from Department of Labor mentioned

**Thai Requirement:**

Electrical installation >15 kVA must have:

1. Design approval (before installation)

2. Installation supervision by licensed engineer

3. Final inspection by Dept of Labor

**Recommendation:**

Confirm electrical design was approved

Verify final electrical inspection scheduled before ops (Permit 9 completion)

This gates operations - cannot operate without electrical approval

---

## MISSING PERMIT 6: Fire Safety Final Inspection

**Guide Reference:** Part 3, Section 3.7 (Fire Safety)

**Status in Your Project:** NOT EXPLICITLY TRACKED

Likely covered under Permit 2 (Building Occupancy Certificate)

But should have separate Fire Department inspection and certification

**Thai Requirement:**

Fire Department inspection before occupancy

Fire detection and suppression systems tested

Emergency exits verified

Staff training documented

**Recommendation:**

Confirm fire safety inspection completed

Certificate should be filed with building occupancy (Permit 2)

---

## MISSING PERMIT 7: Import/Customs Permits

**Guide Reference:** Part 8 (Customs & Import)

**Status in Your Project:** NOT TRACKED

If equipment imported: Customs clearance required

If BOI approved: Duty exemptions apply

If not tracked: May indicate equipment already imported or local sourcing

**Recommendation:**

Verify all equipment imports properly cleared through customs

If BOI approved: Duty exemption documentation should be filed

If not imported: No action needed

---

## MISSING PERMIT 8: Work Permits for Foreign Staff

**Guide Reference:** Part 7 (Labor & Employment Permits)

**Status in Your Project:** NOT TRACKED

If foreign management team: Individual work permits required

Each employee needs separate approval

**Timeline:** 1-2 weeks per employee (after BOI or FBL approval)

**Recommendation:**

If foreign staff planned: Initiate work permits immediately

Coordinate with Immigration Bureau

Can be done in parallel with other permits

---

# SECTION 3: CRITICAL PATH ANALYSIS FOR YOUR PROJECT

## Your Current Critical Path

```

Building Cert (Permit 2)     Operations Permit      Operational

IEAT 02/6                    IEAT 03/2             Start

│                            │                      │

├─ POA: Aug 15              ├─ POA: Nov 19        Jan 27, 2027

├─ Submit: Oct 14           ├─ Submit: Dec 23

├─ Receive: Jan 27, 2027    ├─ Receive: Jan 22

│                           │

└─────────────────────────────┘ GATES EVERYTHING

```

**Critical Observation:**

Building Cert (Permit 2) and Operations Permit (Permit 9) are SYNCHRONIZED

Both due Jan 27, 2027

**RISK:** Any delay in Building Cert = automatic operations delay

**MITIGATION:** These must stay locked together

## Current Schedule Status vs. Guide

**Assessment:** Your schedule is COMPRESSED compared to typical 24-32 months, but within feasible range if:

1. Building Cert stays on track (CRITICAL)

2. All inspections scheduled before late Dec

3. Final systems testing completed by Jan 27

---

# SECTION 4: RISK ASSESSMENT & RECOMMENDATIONS

## HIGH RISK ITEMS

**Risk #1: Building Occupancy Certificate Delay** 🔴

**Action Items:**

[ ] Schedule pre-inspection with AHJ for August

[ ] Document all building systems compliance NOW (don't wait for Oct submission)

[ ] Identify inspection bottlenecks early

[ ] Have contingency plans if Jan 27 slips to Feb/Mar

---

**Risk #2: Water/Wastewater Timeline Compression** 🟡

**Action Items:**

[ ] Finalize water/wastewater design by July 15 (buffer before Aug 9 submission)

[ ] Secure equipment orders now (treatment systems take 4-6 weeks)

[ ] Designate WHA liaison (reduce coordinate delays)

---

**Risk #3: Generator/Fuel Storage Inspection Delays** 🟡

**Action Items:**

[ ] Monitor Cummins/UBC coordination monthly

[ ] Plan emissions testing early (not last minute)

[ ] Budget for potential re-testing (THB 20-50K)

---

**Risk #4: Missing Environmental Compliance** 🔴

**Action Items:**

[ ] **IMMEDIATE:** Confirm EIA status and get approval certificate

[ ] Document all EIA mitigation measures implementation

[ ] Budget for 5-year annual monitoring (THB 250-500K total)

[ ] Establish environmental management system

---

## MEDIUM RISK ITEMS

**Risk #5: Health Harmful Permit (Aor Por 1) Classification** 🟡

Clarify necessity with AHJ

Some facilities may not actually need this

Could be consolidated with other approvals

**Risk #6: Waste Disposal Planning** 🟡

Very late in schedule (Dec)

Identify waste contractors now (limited capacity)

Budget: THB 100-300K annually

**Risk #7: NBTC/Telecom Licensing Scope** 🟡

Clarify what "other licensing" by 3rd party covers

If ISP service: simple

If gateway service: complex

If international: very complex

---

# SECTION 5: RECOMMENDATIONS BY PRIORITY

## IMMEDIATE (This Month - June 2026)

1. **CONFIRM MISSING PERMITS** 🔴

- [ ] BOI Certificate status (required for tax/work permits)

- [ ] EIA Approval status (required for building permit validity)

- [ ] FBL status (if foreign-owned and commercial)

- [ ] Main Building Permit status (vs. just water tank permit)

2. **ACCELERATE BUILDING CERT PREP** 🔴

- [ ] Start gathering all building compliance documents now

- [ ] Schedule pre-inspection with AHJ (identify issues early)

- [ ] Confirm IEAT 02/6 form availability and requirements

- [ ] Assign point person for AHJ coordination

3. **LOCK BUILDING CERT TIMELINE** 🔴

- [ ] Confirm Aug 15 POA can be met

- [ ] Confirm Oct 14 submission is realistic

- [ ] Identify what holds up 3-month approval tail (Oct-Jan)

- [ ] If delays likely, escalate now (don't wait until August)

4. **ENVIRONMENTAL COMPLIANCE CHECK** 🔴

- [ ] Get EIA Approval certificate (if required)

- [ ] Budget for environmental monitoring (5+ years): THB 250-500K

- [ ] Verify all mitigation measures implementation planned

- [ ] Establish environmental management system

## SECOND PRIORITY (July-August 2026)

5. **FINALIZE WATER/WASTEWATER DESIGNS** 🟡

- [ ] Complete detailed water intake design

- [ ] Complete wastewater treatment system design

- [ ] Complete stormwater drainage design

- [ ] Submit all to WHA by Aug 9 (allow buffer)

6. **SECURE EQUIPMENT PROCUREMENT** 🟡

- [ ] Water treatment equipment (4-6 week lead time)

- [ ] Wastewater treatment system (6-8 week lead time)

- [ ] Long-lead electrical equipment

- [ ] Orders must be placed by Aug 1

7. **ELECTRICAL SYSTEMS FINALIZATION** 🟡

- [ ] Confirm electrical design approval obtained

- [ ] Schedule final electrical inspection (before Permit 2 submission)

- [ ] Prepare as-built electrical documentation

8. **FIRE SAFETY SYSTEMS** 🟡

- [ ] Fire detection system tested and commissioned

- [ ] Fire suppression system tested and commissioned

- [ ] Emergency lighting and exits verified

- [ ] Schedule fire department inspection (Aug-Sep)

## THIRD PRIORITY (September-November 2026)

9. **OPERATIONAL PERMITS PREP** 🟡

- [ ] Waste disposal plan finalized

- [ ] Identify licensed waste contractors

- [ ] Health/safety procedures documented

- [ ] Operations manual prepared

10. **FINAL INSPECTIONS & TESTING** 🟡

- [ ] Building final inspection (Aug-Sep, before Oct submission)

- [ ] Fire safety final inspection

- [ ] Electrical final inspection

- [ ] All systems commissioning & testing

11. **FOREIGN STAFF WORK PERMITS** 🟡

- [ ] Prepare work permit documentation

- [ ] Initiate applications (if not already done)

- [ ] Timeline: 1-2 weeks per employee

---

# SECTION 6: CONTINGENCY & MITIGATION STRATEGIES

## If Building Certificate Slips Past January 27

**Scenario:** IEAT 02/6 not approved until Feb/Mar 2027

**Cascade Effects:**

Operations Permit (Permit 9) cannot be approved

Cannot legally operate facility

Revenue loss: ~THB 10-50M per month (depending on capacity)

**Mitigation Strategies:**

1. **Partial Occupancy:** Can some portions operate under separate certificates?

2. **Temporary Operations:** Can interim operations license be obtained while final approval pending?

3. **Parallel Processing:** Request expedited operations permit if building cert still in review

4. **Alternative Approval Path:** Can operations proceed under different regulatory path?

**Recommendation:**

Have contingency operations plan by Aug 2026

Identify regulatory workarounds early with AHJ

---

## If EIA Conditions Weren't Tracked

**Scenario:** EIA approved but mitigation measures not implemented

**Risk:**

ONEP can impose fines (THB 100-500K+)

Permit suspension

Operations interruption

**Mitigation:**

1. Get EIA approval certificate immediately

2. Inventory all conditions and mitigation measures

3. Create implementation tracking sheet

4. Verify each measure is designed/built/operational

5. Document compliance monthly

6. File annual reports with ONEP

**Budget Impact:**

Retrofit mitigation: THB 500K-5M (if not done)

Annual monitoring: THB 50-100K/year

Compliance management: THB 20-30K/year

---

## If Water Supply Insufficient

**Scenario:** WHA capacity cannot meet your demand

**Options:**

1. **Reduce Demand:** Optimize cooling system efficiency (PUE improvement)

2. **Water Recycling:** Increase cooling tower cycles of concentration

3. **Groundwater:** Extract groundwater (requires separate permits)

4. **Reclaimed Water:** Use treated wastewater for makeup

5. **Phase Operations:** Limit operations until additional water available

**Timeline Impact:** 2-3 months if supply-side changes needed

---

# SECTION 7: DOCUMENT CHECKLISTS FOR UPCOMING PERMITS

## Checklist for Permit 2 Submission (Oct 14)

**Submit to: AHJ/IEAT**

[ ] Power of Attorney (signed, sealed)

[ ] Company Affidavit (signed, sealed)

[ ] Land Title Deed copies (certified)

[ ] Original Building Permit (IEAT 02/2 for tank)

[ ] Architectural Plans (updated, final)

[ ] Structural Calculations & Drawings

[ ] Electrical as-built drawings (final inspection complete)

[ ] HVAC/MEP systems commissioning reports

[ ] Fire Safety System certification (final inspection)

[ ] Environmental Compliance documentation

[ ] Occupancy verification photos

[ ] Operations manual (preliminary)

[ ] Staff training documentation

[ ] Building code compliance checklist (signed by engineer)

**Timeline:** Start gathering docs by Aug 1, finalize by Oct 1

---

## Checklist for Building Final Inspection (Aug-Sep 2026)

**Coordinate With: AHJ Inspector**

Structural:

[ ] Building structure inspected

[ ] Roof integrity verified

[ ] Walls and doors compliant

Fire Safety:

[ ] Detection system tested

[ ] Suppression system tested

[ ] Emergency lighting functional

[ ] Exits clear and marked

[ ] Fire-rated walls/doors intact

Electrical:

[ ] All circuits functional

[ ] Grounding verified

[ ] Load calculations met

[ ] Safety switches operational

[ ] Final inspection passed

HVAC:

[ ] Systems operational

[ ] Temperature/humidity controls functional

[ ] Maintenance access clear

Plumbing:

[ ] Water system functional

[ ] Drainage system functional

[ ] Wastewater treatment active

---

# SECTION 8: COST SUMMARY FOR MISSING/UNCERTAIN PERMITS

If permits/compliance items were missed or not tracked:

**Total Contingency Budget:** 1-6M THB (if multiple items were missed)

---

# FINAL RECOMMENDATIONS

## What's Going Well ✅

1. Infrastructure permits on track (power, water, wastewater)

2. Generator licensing well-managed (Cummins/UBC coordination)

3. Timelines realistic for facility operations

4. Document checklists prepared (house reg, utilities)

## What Needs Attention ⚠️

1. Building Certificate timeline is compressed (Oct-Jan) - verify feasibility now

2. Missing critical permits (BOI, EIA, FBL) - confirm status immediately

3. Environmental compliance tracking missing - get EIA docs and budget

4. Waste disposal very late in schedule - plan contractors now

5. Operations Permit depends entirely on Building Cert - lock timeline

## Critical Actions (Next 30 Days)

1. [ ] Confirm BOI, EIA, FBL status (get certificates)

2. [ ] Schedule Building Cert pre-inspection with AHJ (Aug)

3. [ ] Lock Water/Wastewater design submissions (by Aug 9)

4. [ ] Verify all missing permits identified in Section 2

5. [ ] Establish environmental management plan (5-year budget)

6. [ ] Create detailed critical path schedule (with dependencies)

7. [ ] Assign permit managers and escalation procedures

8. [ ] Begin preliminary Building Cert document gathering

---

**This analysis is current as of June 30, 2026. Recommend quarterly review and update as permits progress.**